## Blad1
Functionality check | Interlock description | Signal name | Reset Method | Opmerkingen / vragen | Override to Emergency | Local Evacuation Alarm | RSS Alarm FELIX | RSS Alarm FLARE | RSS AlWarning FELIX | RSS AlWarning FLARE | RSS Warning FELIX | RSS Warning FLARE | BIS Warning | BIS Alarm | FCS Warning FELIX | FCS Warning FLARE | FCS Alarm FELIX | FCS Alarm FLARE | FELIX-HV-RF | FELIX Timing | FLARE-HV | FLARE-RF | FLARE Timing | RSS Warning LED | RSS Alarm LED | GPRS RSS Warning | GPRS RSS Alarm | Visual alarm FEL Areas | Acoustic alarm FEL Areas | Visual alarm Ground Floor | Acoustic alarm Ground Floor | Other
| _1 RSS Warning |  |  |  | 0
| _2 RSS Alarm |  |  |  | 0
| Door emergency FEL Areas | EmergencyOpener.Door01-04 | K |  | X | B | [12 empty] | X | X | X | X | X |  | A |  | A | A | A
| Fire alarm basement | FireAlarm.FELBasement.Safe | K | Alles beneden excl. FEL Areas | X | [13 empty] | X | X | X | X | X
| Fire alarm electronics corridor | FireAlarm.ElectrCorridor.Safe | K |  | X | [13 empty] | X | X | X | X | X
| Fire alarm FEL areas | FireAlarm.FELAreas.Safe | K |  | X | [13 empty] | X | X | X | X | X
| Fire alarm groundfloor | FireAlarm.FELGroundLevel.Safe | K | Hele bovenbouw | X | [13 empty] | X | X | X | X | X
| Fire extinguisher 1/2 active | FireAlarm.Extinguisher.NotActive | K | In geval van handmatig activeren gasblussing is dit noodzakelijk | X | [13 empty] | X | X | X | X | X |  | ? |  | ?
| Fluorine alarm userlab-1 | GDS.FluorineAlarm.UserLabs | K |  | X | [8 empty] | X |  |  |  |  | X | X | X | X | X
| Fluorine alarm userlab-2 | GDS.FluorineAlarm.UserLabs | K |  | X | [8 empty] | X |  |  |  |  | X | X | X | X | X
| Oxygen alarm FEL Areas | GDS.OxygenAlarm.Basement | K |  | X | [8 empty] | X |  |  |  |  | X | X | X | X | X | [8 empty] | GPRS BIS
| Oxygen alarm userlab-1 | GDS.OxygenAlarm.Basement | K |  | X | [8 empty] | X |  |  |  |  | X | X | X | X | X | [8 empty] | GPRS BIS
| Oxygen alarm userlab-2 | GDS.OxygenAlarm.Ground | K |  | X | [8 empty] | X |  |  |  |  | X | X | X | X | X
| ARMD Vault not alive | ARMD-Vault.ReallyAlive | B |  |  |  | NR | NR | [10 empty] | x | x | x | x | x |  | NR |  | NR
| ARMD FLUKE not alive | ARMD-FLUKE.Alive | B |  |  |  | R | R | [10 empty] | X | X | X | X | X |  | R |  | R
| ARMD FTA not alive | ARMD-FTA.Alive | B |  |  |  | R | R | [10 empty] | X | X | X | X | X |  | R |  | R
| ARMD FEL-3 not alive | ARMD-FH.Alive | B |  |  |  | R | R | [10 empty] | X | X | X | X | X |  | R |  | R
| BIS not alive | BIS.Alive | B |  |  |  | X | X | [5 empty] | X |  |  |  |  | X | X | X | X | X |  | A |  | A
| Door breach | StateOverride.DoorBreach | K |  |  | BV | X | X | [10 empty] | X | X | X | X | X |  | A |  | A | A
| Emergency stop FEL Areas | EmergencyStop.LINAC.OK | K |  | X | BV | X | X | [10 empty] | X | X | X | X | X |  | A |  | A | A
| Error State 1-7 | <error1-7> | B |  |  |  | X | X | [10 empty] | X | X | X | X | X | A
| FELIX-PFN Alarm | PFN.FireAlarm.SystemSafe | K |  |  | B | X | X | [10 empty] | X | X | X | X | X |  | A |  | A | A | A
| Get/Set error | GetSetError.* | B |  |  |  | X | X |  |  |  |  | X | [5 empty] | X | X | X | X | X |  | A |  | A
| Ventilation Status not OK | BIS.Ventilation.StatusOK | B | Dit is een check op de inblaas-/afzuigkast |  |  | X | X | [10 empty] | X | X | X | X | X |  | A |  | A |  |  |  |  | extra GPRS BIS
| Water Hazard in FEL Vault | BIS.WaterHazard.Vault | K |  |  |  | X | X | [10 empty] | X | X | X | X | X |  | A |  | A |  |  |  |  | extra GPRS BIS
| Water Hazard in FTA | BIS.WaterHazard.FTA | K |  |  |  | X | X | [10 empty] | X | X | X | X | X |  | A |  | A |  |  |  |  | extra GPRS BIS
| FELIX Fires when not allowed | MK != run AND FELIX.SetRelease all false AND FELIX.BLM.FELFires | K |  |  | B | X | [11 empty] | X | X | - | - | - |  | A |  | A | A | A
| FLARE Fires when not allowed | FLARE.SetRelease all false AND FLARE.BLM.FELFires | K |  |  | B |  | X | [10 empty] | - | - | X | X | X |  | A |  | A | A | A
| Emergency stop FELICE Hall | EmergencyStop.FH.OK | B | [5 empty] | X | X | [8 empty] | - | X | - | - | X |  | A |  | A
| Emergency stop userlab-1 | EmergencyStop.UserLab1.OK | B | [5 empty] | X | X | [8 empty] | - | X | - | - | X |  | A |  | A
| Emergency stop userlab-2 | EmergencyStop.UserLab2.OK | B | [5 empty] | X | X | [8 empty] | - | X | - | - | X |  | A |  | A
| ARMD FEL-3 alarm (no) | ARMD-FH.NoAlarmNo | B |  |  | G |  |  |  |  | E | E | [6 empty] | (X) | X | (X) | (X) | (X) |  | A |  | A |  |  | (A) | (A)
| ARMD FEL-3 alarm (restricted) | ARMD-FH.NoAlarmRestricted | B |  |  | G |  |  |  |  | E | E | [6 empty] | (X) | (X) | (X) | (X) | (X) |  | A |  | A |  |  | (A) | (A)
| ARMD FLUKE alarm (no) | ARMD-FLUKE.NoAlarmNo | B |  |  | G |  |  |  |  | E | E | [6 empty] | (X) | X | (X) | (X) | X |  | A |  | A |  |  | (A) | (A)
| ARMD FLUKE alarm (restricted) | ARMD-FLUKE.NoAlarmWarning | B |  |  | G |  |  |  |  | E | E | [6 empty] | (X) | (X) | (X) | (X) | (X) |  | A |  | A |  |  | (A) | (A)
| ARMD FTA alarm (no) | ARMD-FTA.NoAlarmNo | B |  |  | B |  |  |  |  | E | E | [6 empty] | (X) | X | (X) | (X) | (X) |  | A |  | A | (A) | (A)
| ARMD FTA alarm (restricted) | ARMD-FTA.NoAlarmRestricted | B |  |  | B |  |  |  |  | E | E | [6 empty] | (X) | (X) | (X) | (X) | (X) |  | A |  | A | (A) | (A)
| Emergency stop HFML | EmergencyStop.HFML.OK | B | [7 empty] | X | X | [6 empty] | - | X | - | - | X | A |  | A
| FireAlarm system not alive | FireAlarm.System.Alive | B | [7 empty] | X | X | [6 empty] | - | X | - | - | X
| Fluorine alarm system not alive | GDS.Unit.Alive | B | [7 empty] | X | X | [6 empty] | - | X | - | - | X
| Oxygen alarm system not alive | GDS.Unit.Alive | B | [7 empty] | X | X | [6 empty] | - | X | - | - | X
| BLM FELIX off in restricted access | <restricted> implies FELIX.BLM.InNormalMode | B | [7 empty] | R | [7 empty] | - | X | - | - | - | R |  | R
| Door breach D9 | Door09.DoorBreach | K,FH | uitzondering |  | GV |  |  |  |  | X | [7 empty] | - | X | - | - | - | A |  | A |  |  |  | A
| Door emergency FELICE Hall | EmergencyOpener.Door09 | K |  |  | G |  |  |  |  | X | [7 empty] | - | X | - | - | - |  | A |  | A |  |  | A | A
| FELIX FCS not alive | FELIX.FCS.Alive | B | [7 empty] | R | [7 empty] | - | X | - | - | - | R |  | R
| BLM FLARE alarm | FLARE.BLM.NoAlarm | B | [8 empty] | X | [6 empty] | - | - | - | - | X | A |  | A
| BLM FLARE not alive | FLARE.BLM.Alive | B | [8 empty] | X | [6 empty] | - | - | - | - | X | A |  | A
| BLM FLARE off in restricted access | <restricted> implies FLARE.BLM.InNormalMode | B | [8 empty] | R | [6 empty] | - | - | - | - | X | R |  | R
| FLARE Dump temperature too high | Dump.TempNotHigh | B | [8 empty] | X | [6 empty] | - | - | - | - | X | A |  | A
| FLARE FCS not alive | FLARE.FCS.Alive | B | [8 empty] | R | [6 empty] | - | - | - | - | X | R |  | R
| BIS warning | BIS.NoWarning | B | [9 empty] | X | [5 empty] | - | - | - | - | - | [8 empty] | GPRS BIS
| BIS alarm | BIS.NoAlarm | B | [10 empty] | X |  |  |  |  | - | X | - | - | X | [8 empty] | GPRS BIS
| FLARE Dump water flow too low | BIS.DumpWater.FlowNotLow | B | [8 empty] | X |  | X |  |  |  |  | - | - | - | - | X | A |  | A
| FLARE Dump water temperature too high | BIS.DumpWater.TempNotHigh | B | [8 empty] | X |  | X |  |  |  |  | - | - | - | - | X | A |  | A
| FELIX FCS alarm | FELIX.FCS.NoAlarm | B | [13 empty] | R |  | - | X | - | - | -
| FLARE FCS alarm | FLARE.FCS.NoAlarm | B | [14 empty] | R | - | - | - | - | X
| ACS not alive | ACS.Alive | B | Check (met EAL?) wat de vossessor nog doet als ACS not alive er is. | [7 empty] | X | [6 empty] | - | - | - | - | - | A |  | A
| FELIX FCS warning | FELIX.FCS.NoWarning | B | [11 empty] | R |  |  |  | - | - | - | - | -
| FLARE FCS warning | FLARE.FCS.NoWarning | B | [12 empty] | R |  |  | - | - | - | - | -
| StartUpAlarm | RSS.StartUpAlarm | - |  |  | BG | [12 empty] | - | - | - | - | - |  |  |  |  | A | A | A | A
| SweepInvalid | Sweep.Invalid | MK=off | depends on where you are in the sweep |  | B/G | [12 empty] | - | - | - | - | - | [5 empty] | 3x |  | 3x
| ZZZ ARMD FLUKE warning | ARMD-FLUKE.NoWarning | B |  |  | G | [23 empty] | A | A
Legend:
A = always
R = only in <run> and <run&fired>
NR = not in <run> or <run&fired>
E = exceptional
Local Evacuation alarms:
B(V) basement (visual only)
G(V) ground level (visual only)
Note on AK25: Flare-Admin: Wel bellen maar dan vervolgens niks zien op het controle paneel?
Note on AK26: Flare-Admin: Wel bellen maar dan vervolgens niks zien op het controle paneel?
Note on AK27: Flare-Admin: Wel bellen maar dan vervolgens niks zien op het controle paneel?
Note on C30: Flare-Admin: Estop FH moet de cleared.FH resetten en D09 ontgrendelen Feedback Frans: Krijg je een lokaal anders access state, druk de groen drukker maar door in zo'n situatie
Note on AC45: Bryan: Gaat nooit af, moet wel om de operator alert te maken, uitzondering Rienk
Note on AE45: Bryan: Gaat nooit af, moet wel om de operator alert te maken, uitzondering Rienk
Note on AE53: Bryan: Triggerde GPRS RSS Alarm maar is niet logisch na overleg met Rienk
Note on W54: Flare-Admin: Is er een gecombineerd koelwater systeem voor de dumps? Of als dump flare te heet wordt alleen FLARE pauzeren?
Note on W55: Flare-Admin: Is er een gecombineerd koelwater systeem voor de dumps? Of als dump flare te heet wordt alleen FLARE pauzeren?
Note on Z58: Flare-Admin: Komt omdat RSS warning Timing afschakeld van FLARE